## 2019 Energy Model Results
Project Name: | P-1458 |  |  | CLIMATE ZONE | 3A
Project Location: | Jacksonville, North Carolina |  |  | BUILDING TYPE | Office
Date: | 2024-05-09 |  |  | BPF | 0.53
SC Project No.: | 23144
INPUTS | [8 empty] | Calcs
Model | BBP ($) | ELECTRICITY (kwh) | GAS (Therms) | TOTAL (Kwh) | PROCESS (Kwh) | RECEPTACLES (Kwh) | BBUEC ($) | BBREC ($) | Performance Cost Index Target
Baseline | 89078 | 1256040 | 0 | 1256039.6993 | 92424 | 37864 | 9239.9902 | 79838.0098 | 0.57875
| INPUTS | Calcs
Model | PROPOSED BUILDING PERFORMANCE ($) | Performance Cost Index | Ashrae Savings (%)
Proposed | 48488 | 0.54433 | 5.9474
LINK TO REFERENCE

## Climate Zone (hidden)
TYPE | 0A | 1A | 0B | 1B | 2A | 2B | 3A | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 5C | 6A | 6B | 7 | 8
Multifamily | 0.68 | 0.68 | 0.7 | 0.7 | 0.66 | 0.66 | 0.69 | 0.68 | 0.59 | 0.74 | 0.76 | 0.74 | 0.7 | 0.73 | 0.75 | 0.68 | 0.71 | 0.68 | 0.72
Helthcare / Hospital | 0.6 | 0.6 | 0.6 | 0.6 | 0.58 | 0.54 | 0.56 | 0.55 | 0.55 | 0.55 | 0.54 | 0.54 | 0.57 | 0.52 | 0.54 | 0.57 | 0.52 | 0.57 | 0.57
Hotel / Motel | 0.55 | 0.55 | 0.53 | 0.53 | 0.53 | 0.52 | 0.53 | 0.54 | 0.54 | 0.53 | 0.53 | 0.52 | 0.5 | 0.51 | 0.51 | 0.5 | 0.51 | 0.5 | 0.5
Office | 0.52 | 0.52 | 0.57 | 0.57 | 0.5 | 0.56 | 0.53 | 0.56 | 0.48 | 0.51 | 0.52 | 0.49 | 0.51 | 0.51 | 0.49 | 0.52 | 0.51 | 0.49 | 0.51
Restaurant | 0.63 | 0.63 | 0.64 | 0.64 | 0.6 | 0.6 | 0.6 | 0.61 | 0.58 | 0.62 | 0.57 | 0.61 | 0.63 | 0.6 | 0.64 | 0.65 | 0.62 | 0.67 | 0.07
Retail | 0.51 | 0.51 | 0.54 | 0.54 | 0.49 | 0.55 | 0.51 | 0.55 | 0.53 | 0.51 | 0.55 | 0.51 | 0.5 | 0.51 | 0.55 | 0.5 | 0.51 | 0.48 | 0.5
School | 0.39 | 0.39 | 0.47 | 0.47 | 0.38 | 0.43 | 0.38 | 0.42 | 0.4 | 0.37 | 0.4 | 0.38 | 0.36 | 0.4 | 0.36 | 0.36 | 0.37 | 0.36 | 0.37
Warehouse | 0.38 | 0.38 | 0.42 | 0.42 | 0.4 | 0.42 | 0.43 | 0.44 | 0.43 | 0.44 | 0.43 | 0.46 | 0.49 | 0.47 | 0.48 | 0.54 | 0.51 | 0.57 | 0.57
All Others | 0.56 | 0.56 | 0.57 | 0.57 | 0.5 | 0.52 | 0.5 | 0.54 | 0.53 | 0.53 | 0.51 | 0.54 | 0.51 | 0.51 | 0.5 | 0.5 | 0.5 | 0.5 | 0.46

## 2013 Energy Model Results
Project Name:
Project Location:
Date:
SC Project No.:
| INPUTS |  |  |  |  | RESULTS SUMMARY
| ELECTRICITY | GAS |  | PROCESS & RECEPTACLES |  | EPACT SAVINGS | ASHRAE 90.1 SAVINGS | LEED SAVINGS | Co2e EMISSIONS | Co2e EMISSIONS SAVINGS
SPPN | kwh | Therms | btu | process kwh | process btu | PROPOSED % SAVINGS | ASHRAE % savings | LEED % savings* | CO2e Emissions (CO2e lbs) | CO2e Emissions % savings
Proposed | 406728 | 23682 | 3756013542.1597 | 150815 | 514602140.4005 | 15.48% | 13.65% | 28.43% | 1033201.7233 | 51.47%
Baseline | 1274787 | 0 | 4349753796.0729 | 150815 |  |  |  |  | 2128894.29
*Based on $/Kwh and $/Therm
***Note:

## Notes For 30% Savings
TYPE | Item to Check | Description | Checked ?
Cooling | Cooling capacity | Even though the unit scehduled maybe higher capacity, the model should show the capacity closer to the actual load. Increase the LAT to meet the load at the CFM provided.
Cooling | DCV | If there are any zones that have the a CO2 sensor, use DCV checkmark in the zone under mecahnical
Cooling | DCV with occupancy | If we are doing OCC sensor DCV, check this under mechanical tab in zones
Cooling | Occupancy | Check that the occupancy is modeled correctly. Under the general zone tab. If it is incorrect, find and replace needs to be done to make sure all the numbers are reset.
Cooling | Room Temp | The room temp under each room must be accurate to the design.
Cooling | Packaged DX | For packaged DX unit, a custom curve with different power consumption can be used.
Cooling | Packaged DX | Packaged DX system's efficiency shall be added on the cooling tag
Cooling | Economizer | Economizer operation must be selected. If applicable check ASHRAE or T-24
Cooling | Energy Recovery | If the project has an energy revocery wheel, this will be modeld in the Outdoor air section of the system tab.
Cooling | Chiller Custom Curve | Chiller custom curve can be modeled for better savings in the chiller curves section. Reach out to the equipment manufacturer for data at various part loads
Cooling | Chiller Variable Primary | Model the variable primary pumps as secondary pumps. The primary pumps in E-pro are comnsidered as powered by the chiller.
Fans | Fan Power | This will be the fan power. Not the total HP. Prorate the BHP for the space if it is only serving a part of the spaces
Fans | VFD on fans | Make sure VFD is modeled if the fan is supposed to be variable.
Fans | Airflow | The airflow must be the design airflow of the fan
Fans | Fan type | The fan, blow through or draw through should be selected accordingly
Fans | Zone Exhaust | Exhaust fans will get modeled under each zone under mechanical. Proprate the fan BHP
General | Area of the Building | Check the total area on the AHUs and modeled in E-pro matches with the excel or Revit
General | Systems | Check if all the systems scheduled on the Mecahnical scehdules are modeled in the E-pro. Usually split systems get missed.
General | Systems
General | Rooms | Check if the U values match the prescriptive reuqirements or the performance values provided by the architect
Heat Rejection | Applicability | This should only be visible if you have a cooling tower
Heating | Freeze Protection | Do not model any freeze protection coils
Heating | Terminal Units | model all BTUs for all Reheat coils in the zonal system
Heating | Terminal Units Min | The minimum of the VAV should be 30% generally with exceptions.
Heating | LAT | Heating LAT needs to be corrected.
Heating | Coil control | Change various coil control in systems tab to see which one yields the best result.
heating | Packaged DX | Packaged DX system's efficiency shall be added on the heating tag
Lighting | Savings | 30% savings shall be provided by the lighting designer. Coordinate with PM to confirm
Pumps | Design power | Use the pump power from design. Use the BHP.