## Setpoints_Requirements
Design Requirements Table
System | Compliance Rrequirement | Related to | Setpoints to be defined | Notes
General | All | Zone | Zone temperature | Based on zone types such as VAV, mech room, telecom room etc. Must show the occupied and unoccupied setpoint
General | Title 24 | Outside Air | Vocc_min, Varea_min, OS | Basically area based, occupancy based and where occupancy standby mode is allowed.
General | ASHRAE 90.1 | Outside Air | Vbz, Ez, OS | If our table from excel is included on the drawigns, these values are defined.
General | Title 24 | Outside Air | CO2 Setpoint | CO2 setpoint for all occupancy types is 1000 ppm
General | ASHRAE 90.1 | Outside Air | CO2 Setpoint | Add a note somewhere to provide per ASHRAE standard 62.1
VAV Terminal Unit | All

## Points_Lists
VAV TERMINAL UNIT WITH REHEAT
Required | Description | Device | Type
CO2 DCV | Zone CO2 level | Room CO2 sensor | AI
Heating coil | Heating signal | Modulating valve | AO
Heating coil | Heating signal | Floating actuator | DO
Heating coil | Heating signal | Modulating electric heating coil | DO
Heating coil | Discharge air temperature (DAT) | Duct temperature sensor (probe or averaging at designer’s discretion) | AI
Occupancy DCV | Occupancy sensor | Occupancy sensor | DI
R | VAV box damper position | Modulating actuator | AO
R | VAV box damper position | Floating actuator | DO
R | Discharge airflow | Differential pressure (DP) transducer connected to flow sensor | AI
R | Zone temperature | Room temperature sensor | AI
R | VAV box damper position | Modulating actuator | AO
R | VAV box damper position | Floating actuator | DO
Window DCV | Window switch | Window switch | DI
Zone Tstat | Local override | Zone thermostat override switch | DI
Zone Tstat | Zone temperature setpoint adjustment | Zone thermostat adjustment | AI
MULTIZONE AHU
Required | Description | Device | Type
Common Econ | Outdoor airflow | Airflow measurement station (AFMS) | AI
Economizer | Economizer outdoor air damper | Modulating actuator | AO
Electric Preheating coil | Heating signal | Modulating electric heating coil | AO
Electric Reheating coil | Heating signal | Modulating electric heating coil | AO
Final Filter | Filter pressure drop | DP transducer across filter | AI
High Static Reset | Supply fan high static alarm reset | Dry contact to 120 or 24 V control circuit | DO
Intermidiate Filter | Filter pressure drop | DP transducer across filter | AI
Prefilter | Filter pressure drop | DP transducer across filter | AI
Preheating coil | Heating signal | Modulating HW valve | AO
R | Supply fan start/stop | Connect to VFD Run | DO
R | Supply fan speed | Connect to VFD Speed | AO
R | Supply fan status | Connect to VFD Status | DI
R | Supply air temperature | Duct temperature sensor (probe or averaging at designer’s discretion) | AI
R | Duct static pressure (DSP) | DP transducer down duct | AI
R | Heating coil supply air temperature | Averaging temperature sensor | AI
R | Return air damper | Modulating actuator | AO
R | Outdoor air temperature | Temperature sensor at outdoor air intake | AI
R | Mixed air temperature | Averaging temperature sensor | AI
R | Return air temperature | Duct temperature sensor | AI
R | Cooling signal | Modulating CHW valve | AO
Reheating coil | Heating signal | Modulating HW valve | AO
Relief Damper | Relief damper open/close | Modulating actuator | AO
Relief Damper | Building static pressure | DP transducer between representative space and outdoors | AI
Relief Fan | Relief-fan start/stop | Connect to VFD Run | DO
Relief Fan | Relief-fan status | Connect to VFD Status | DI
Relief Fan | Relief-fan speed | Connect to VFD Speed | AO
Relief Fan | Relief damper open/close | Two position actuator | DO
Relief Fan | Building static pressure | DP transducer between representative space and outdoors | AI
Retrun Fan | Return fan start/stop | Connect to VFD Run | DO
Retrun Fan | Return-fan status | Connect to VFD Status | DI
Retrun Fan | Return-fan high-static alarm reset | Dry contact to 120V or 24V control circuit | DO
Retrun Fan | Return-fan speed | Connect to VFD Speed | AO
Return Fan Airflow Tracking | Supply airflow (if airflow tracking logic used) | Airflow measurement station at supply fan (or sum of VAV zones) | AI
Return Fan Airflow Tracking | Return airflow (if airflow tracking logic used) | Airflow measurement station at return fan | AI
Return Fan Building Static | Return-fan discharge static pressure | DP transducer at fan | AI
Return Fan Building Static | Exhaust damper | Modulating actuator | AO
Return Fan Building Static | Building static pressure | DP transducer between representative space and outdoors | AI
Split Econ | Minimum outdoor air damper | Modulating actuator | AO
Split Econ | Minimum outdoor airflow | Airflow measurement station | AI
SINGLE ZONE AHU
Required | Description | Device | Type
CO2 DCV | Zone CO2 level | Room CO2 sensor | AI
DX | Cooling signal | Variable-capacity compressor | AO
Final Filter | Filter pressure drop | DP transducer across filter | AI
Hydronic | Cooling signal | Modulating CHW valve | AO
Intermidiate Filter | Filter pressure drop | DP transducer across filter | AI
Occupancy DCV | Occupancy sensor | Occupancy sensor | DI
Outdoor AFM | Outdoor Airflow | Airflow measurement station | AI
Prefilter | Filter pressure drop | DP transducer across filter | AI
Preheat Coil | Heating signal | Modulating HW valve | AO
Preheat Coil Electric | Heating signal | Modulating electric heating coil | AO
R | Supply fan start/stop | Connect to VFD Run | DO
R | Supply fan speed | Connect to VFD Speed | AO
R | Supply fan status | Connect to VFD Status | DI
R | Supply air temperature | Duct temperature sensor (probe or averaging at designer’s discretion) | AI
R | Outdoor/return air damper | Modulating actuators | AO
R | Outdoor air temperature | Temperature sensor at outdoor air intake | AI
R | Mixed air temperature | Averaging temperature sensor | AI
R | Return air temperature | Duct temperature sensor | AI
R | Zone temperature | Room temperature sensor | AI
Reheat Coil | Heating signal | Modulating HW valve | AO
Reheat Coil Electric | Heating signal | Modulating electric heating coil | AO
Relief Damper | Relief damper | Modulating actuator | AO
Relief Fan | Relief-fan start/stop | Connect to VFD Run | DO
Relief Fan | Relief-fan status | Connect to VFD Status | DI
Relief Fan | Relief-fan speed | Connect to VFD Speed | AO
Relief Fan | Relief-damper open/close | Two position actuator | DO
Return Fan | Return fan start/stop | Connect to VFD Run | DO
Return Fan | Return-fan status | Current VFD Status | DI
Return Fan | Return-fan speed | Connect to VFD Speed | AO
Return Fan Airflow Tracking | Exhaust air damper | Two position actuator | DO
Return Fan Building Static | Return Fan Discharge Static Pressure | Differential pressure transducer at fan | AI
Return Fan Building Static | Exhaust Air Damper | Modulating actuator | AO
Return Fan Building Static | Building Static Pressure | Differential pressure transducer between representative space and outdoors | AI
Window DCV | Window switch | Window switch | DI
Zone Tstat | Local override | Zone thermostat override switch | DI
Zone Tstat | Zone temperature setpoint adjustment | Zone thermostat adjustment | AI
CONSTANT SPEED EXHAUST FAN
Required | Description | Device | Type
R | Exhaust Fan Start/Stop | Connect to motor starter | DO
R | Exhaust Fan Status | Current switch | DI
BY TEMP | Zone Temperature | Room temperature sensor | AI

## Sequences
MULTIZONE AHU
Required | Table | table_column | Section title | Section Applicable if | Code | Sequence
yes | Trim_and_Respond_Table | Static Pressure | Supply Fan Control | Applicable | All | Supply Fan Start/Stop a. Supply fan shall run when system is in the Cooldown Mode, Setup Mode, or Occupied Mode. b. If there are any VAV-reheat boxes on perimeter zones, supply fan shall also run when system is in Setback Mode or Warmup Mode (i.e., all modes except unoccupied). c. Totalize current airflow rate from VAV boxes to a software point Vps. 5.16.1.2. Static Pressure Set-Point Reset a. Static pressure setpoint. Setpoint shall be reset using T&R logic (see Section 5.1.14 from ASHRAE guideline 36) using the parameters shown in trim and respond table. Static Pressure Control a. Supply fan speed is controlled to maintain DSP at setpoint when the fan is proven ON. Where the Zone Groups served by the system are small, provide multiple sets of gains that are used in the control loop as a function of a load indicator (such as supply-fan airflow rate, the area of the Zone Groups that are occupied, etc.).
yes | Trim_and_Respond_Table | Supply Air | Supply Air Temperature Control | Applicable | All | Control loop is enabled when the supply air fan is proven ON, and disabled and output set to deadband (no heating, minimum economizer) otherwise. Supply Air Temperature Setpoint 1. Refer to drawings for Min_ClgSAT, Max_ClgSAT, OAT_Min, and OAT_Max setpoints b. During Occupied Mode and Setup Mode, setpoint shall be reset from Min_ClgSAT when the outdoor air temperature is OAT_Max and above, proportionally up to T-max when the outdoor air temperature is OAT_Min and below. b1. T-max shall be reset using T&R logic (see Section 5.1.14 form ASHRAE Guideline 36) between Min_ClgSAT and Max_ClgSAT. The parameters shown in the trim and respond variables table are suggested as a starting place, but they will require adjustment during the commissioning/tuning phase. c. During Cooldown Mode, setpoint shall be Min_ClgSAT. d. During Warmup Mode and Setback Mode, setpoint shall be 35°C (95°F). 2. Supply air temperature shall be controlled to setpoint using a control loop whose output is mapped to sequence the heating coil (if applicable), outdoor air damper, return air damper, and cooling coil as shown in Figure shown. a. The points of transition along the x-axis shown and described in Figures are representative. Separate gains shall be provided for each section of the control map (heating coil, economizer, cooling coil) that is determined by the contractor to provide stable control. Alternatively, the contractor shall adjust the precise value of the x-axis thresholds shown in Figure to provide stable control. Damper control depends on the type of building pressure control system.
yes |  |  | Supply Air Temperature Control | Retun fan | All | b. For units with return fans 1. Return air damper maximum position MaxRA-P is modulated to control minimum outdoor air volume (see Sections related to minimum outdoor air control).
yes |  |  | Supply Air Temperature Control | Relief Fan | All | b. For units with relief dampers or relief fans 1. Economizer damper minimum position MinOA-P and/or return air damper maximum position MaxRA-P are modulated to control minimum outdoor air volume (see Sections related to minimum outdoor air control).
|  |  | Supply Air Temperature Control | Saperate min OA and Econ Damper | All | 2. For units with a separate minimum outdoor air damper, economizer damper minimum position MinOA-P is 0%, and return air damper maximum position MaxRA-P is modulated to control minimum outdoor air volume (see Sections related to minimum outdoor air control).
|  |  | Supply Air Temperature Control | Single Econ and OA damper | All | 2. For units with a single common minimum outdoor air and economizer damper, return air damper maximum position MaxRA-P and economizer damper minimum position MinOA-P are modulated to control minimum outdoor air volume (see Section 5.16.6). Economizer damper maximum position MaxOA-P is limited during minimum outdoor air control (e.g., economizer lockout due to high OAT).
OA Damper |  |  | Minimum Outdoor Airflow Setpoints |  | Title 24 | Outdoor Airflow Setpoint for California Title 24 Ventilation a. See Section 5.2.1.4 for zone outdoor air rates Zone-Abs-OA-min and Zone Des OA min. b. See Section 3.1.4.2.b for setpoints AbsMinOA and DesMinOA. c. Effective outdoor air absolute minimum and design minimum setpoints are recalculated continuously based on the mode of the zones being served. 1. AbsMinOA* is the sum of Zone-Abs-OA-min for all zones in all Zone Groups that are in Occupied Mode but shall be no larger than the absolute minimum outdoor airflow AbsMinOA. 2. DesMinOA* is the sum of Zone-Des-OA-min for all zones in all Zone Groups that are in Occupied Mode but shall be no larger than the design minimum outdoor airflow DesMinOA.
OA Damper |  |  | Minimum Outdoor Airflow Setpoints |  | ahsrae 62.1 | Outdoor Airflow Setpoint for ASHRAE Standard 62.1-2016 Ventilation a. See Section 5.2.1.3 for zone outdoor air requirement Voz. b. See Section 3.1.4.2.a for setpoints DesVou and DesVot. c. The uncorrected outdoor air rate setpoint Vou is recalculated continuously based on the adjusted ventilation rates Vbz-A* and Vbz-P* of the zones being served determined in accordance with Section 5.2.1.3. Calculate the uncorrected outdoor air rate Vou for all zones in all Zone Groups that are in Occupied Mode, but note that Vou shall be no larger than the design uncorrected outdoor air rate DesVou. V_ou=MIN( DesV_ou │(∑▒〖V_(〖bz-A〗^* )+∑▒V_(〖bz-P〗^* ) 〗)) d. Vps is the sum of the zone primary airflow rates Vpz as measured by VAV boxes for all zones in all Zone Groups that are in Occupied Mode. e. For each zone in Occupied Mode, calculate the zone primary outdoor air fraction Zpz: Zpz = Voz/Vpz f. Calculate the maximum zone outdoor air fraction Zp: Zp = max(Zpz) g. Calculate the current system ventilation efficiency Ev: Ev = 1 + (Vou/Vps) – Zp f. Calculate the effective minimum outdoor air setpoint MinOAsp as the uncorrected outdoor air intake divided by the system ventilation efficiency, but no larger than the design total outdoor air rate DesVot: MinOAsp=MIN( V_ou/E_v │ DesV_ot )
OA Damper |  |  | Minimum OA Saperate Damper and airflow tracking
OA Damper |  |  | Minimum OA common Damper and airflow tracking
Relief Damper |  |  | Control of Actuated Relief Dampers without Fans
Relief fan |  |  | Relief fan control
Return Fan |  |  | Building pressure Control
Return Fan |  |  | Airflow tracking Control
Freeze Protection | [5 empty] | If the supply air temperature drops below 4.4°C (40°F) for 5 minutes, send two (or more, as required to ensure that heating plant is active) heating hot-water plant requests, override the outdoor air damper to the minimum position, and modulate the heating coil to maintain a supply air temperature of at least 6°C (42°F). Disable this function when supply air temperature rises above 7°C (45°F) for 5 minutes. If the supply air temperature drops below 3.3°C (38°F) for 5 minutes, fully close both the economizer damper and the minimum outdoor air damper for 1 hour and set a Level 3 alarm noting that minimum ventilation was interrupted. After 1 hour, the unit shall resume minimum outdoor air ventilation and enter the previous stage of freeze protection. If it is warm enough that the SAT rises above 7°C (45°F) with minimum ventilation, the unit will remain in Stage 1 freeze protection for 5 minutes then resume normal operation. Upon signal from the freeze-stat (if installed), or if supply air temperature drops below 3.3°C (38°F) for 15 minutes or below 1°C (34°F) for 5 minutes, shut down supply and return/relief fan(s), close outdoor air damper, open the cooling-coil valve to 100%, and energize the CHW pump system. Also send two (or more, as required to ensure that heating plant is active) heating hot-water plant requests, modulate the heating coil to maintain the higher of the supply air temperature or the mixed air temperature at 27°C (80°F), and set a Level 2 alarm indicating the unit is shut down by freeze protection. If a freeze-protection shutdown is triggered by a low air temperature sensor reading, it shall remain in effect until it is reset by a software switch from the operator’s workstation. (If a freeze-stat with a physical reset switch is used instead, there shall be no software reset switch.)
Alarms
yes |  |  | Automatic Fault Detection and Diagnostics
yes |  |  | Testing or Commissioning Overrides
yes |  |  | Plant Requests

## Tables
Trim_and_Respond_Table
Variable | Definition | Static Pressure | Supply Air
Device | Associated device (e.g., fan, pump) | Supply fan | Supply fan
SP0 | Initial setpoint | 0.5 in. of water | SPmax
SPmin | Minimum setpoint | 0.1 in. of water | Min_ClgSAT
SPmax | Maximum setpoint | Max_DSP (See Schedules for max DP) | Max_ClgSAT
Td | Delay timer | 10 minutes | 10 minutes
T | Time step | 2 minutes | 2 minutes
I | Number of ignored requests | 2 | 2
R | Number of requests from zones/systems | Zone static pressure reset requests | Zone cooling SAT requests
SPtrim | Trim amount | –0.05 in. of water | +0.2°F
SPres | Respond amount (must be opposite in sign to SPtrim) | +0.06 in. of water | –0.3°F
SPres-max | Maximum response per time interval (must be same sign as SPres) | +0.13 in. of water | –1.0°F