## Sheet1
ROOM | ROOM # | AREA (FT²) | HG (FT) | TOTAL AC/HR | 100% EA | CRICU EA | LOAD CFM | AC/HR CFM | 4-A DESIGNATION | AIRBALANCE RELATIONSHIP | MINIMUM OSA CHANGES PER HOUR | OSA CFM | ALL AIR EXHAUSTED | CALCULATED SA CFM | DESIGN SA CFM | RA CFM | EA CFM
DUMMY | 1234 | 100 | 10 | 4 | NR | - | 0 | 70 | PATIENT ROOM | NO REQUIREMENT FOR CONTINUOUS DIRECTIONAL CONTROL | 2 | 40 | NR | 100 | 100 | 100 | 0
DUMMY | 1234 | 200 | 9.5 | 4 | NR | - | 0 | 130 | PATIENT ROOM | NO REQUIREMENT FOR CONTINUOUS DIRECTIONAL CONTROL | 2 | 70 | NR | 200 | 200 | 200 | 0
DUMMY | 1234 | 300 | 10 | 4 | NR | - | 0 | 200 | PATIENT ROOM | NO REQUIREMENT FOR CONTINUOUS DIRECTIONAL CONTROL | 2 | 100 | NR | 300 | 300 | 300 | 0
DUMMY | 1234 | 20 | 10 | 6 | NR | - | 0 | 20 | BLOOD BANK/TISSURE STORAGE | NO REQUIREMENT FOR CONTINUOUS DIRECTIONAL CONTROL | 2 | 10 | NR | 20 | 20 | 20 | 0
DUMMY | 1234 | 36 | 10 | 4 | NR | - | 0 | 30 | PATIENT ROOM | NO REQUIREMENT FOR CONTINUOUS DIRECTIONAL CONTROL | 2 | 20 | NR | 40 | 40 | 40 | 0
DUMMY | 1234 | 212 | 10 | 4 | NR | - | 0 | 150 | PATIENT ROOM | NO REQUIREMENT FOR CONTINUOUS DIRECTIONAL CONTROL | 2 | 80 | NR | 215 | 215 | 215 | 0
DUMMY | 1234 | 27 | 10 | 6 | NR | - | 0 | 30 | BLOOD DRAW/PHLEBOTOMY | NO REQUIREMENT FOR CONTINUOUS DIRECTIONAL CONTROL | 2 | 10 | NR | 30 | 30 | 30 | 0
DUMMY | 1234 | 111 | 10 | 4 | NR | - | 0 | 80 | PATIENT ROOM | NO REQUIREMENT FOR CONTINUOUS DIRECTIONAL CONTROL | 2 | 40 | NR | 115 | 115 | 115 | 0
DUMMY | 1234 | 256 | 10 | 4 | NR | - | 0 | 180 | PATIENT ROOM | NO REQUIREMENT FOR CONTINUOUS DIRECTIONAL CONTROL | 2 | 90 | NR | 260 | 260 | 260 | 0
DUMMY | 1234 | 2347 | 10 | 4 | NR | - | 0 | 1570 | PATIENT ROOM | NO REQUIREMENT FOR CONTINUOUS DIRECTIONAL CONTROL | 2 | 790 | NR | 2350 | 2350 | 2350 | 0
DUMMY | 1234 | 454 | 10 | 4 | NR | - | 0 | 310 | PATIENT ROOM | NO REQUIREMENT FOR CONTINUOUS DIRECTIONAL CONTROL | 2 | 160 | NR | 455 | 455 | 455 | 0
|  | 4063 | [9 empty] | 1410 |  | 4085 | 4085 | 4085 | 0