## Sheet1
ROOM | ROOM # | AREA (FT²) | HG (FT) | TOTAL AC/HR | 100% EA | CRICU EA | LOAD CFM | AC/HR CFM | 1 CFM/SF | 4-A DESIGNATION | AIRBALANCE RELATIONSHIP | MINIMUM OSA CHANGES PER HOUR | OSA CFM | ALL AIR EXHAUSTED | CALCULATED SA CFM | DESIGN SA CFM | RA CFM | EA CFM
DUMMY | 1234 | 1000 | 10 | 4 | NR | - | 0 | 670 | 1000 | PATIENT ROOM | NO REQUIREMENT FOR CONTINUOUS DIRECTIONAL CONTROL | 2 | 340 | NR | 1000 | 1000 | 1000 | 0
DUMMY | 1234 | 1000 | 10 | 4 | NR | - | 0 | 670 | 1000 | PATIENT ROOM | NO REQUIREMENT FOR CONTINUOUS DIRECTIONAL CONTROL | 2 | 340 | NR | 1000 | 1000 | 1000 | 0
DUMMY | 1234 | 1000 | 10 | 4 | NR | - | 0 | 670 | 1000 | PATIENT ROOM | NO REQUIREMENT FOR CONTINUOUS DIRECTIONAL CONTROL | 2 | 340 | NR | 1000 | 1000 | 1000 | 0
DUMMY | 1234 | 567 | 10 | 4 | NR | - | 0 | 380 | 567 | PATIENT ROOM | NO REQUIREMENT FOR CONTINUOUS DIRECTIONAL CONTROL | 2 | 190 | NR | 570 | 570 | 570 | 0
DUMMY | 1234 | 1000 | 10 | 4 | NR | - | 0 | 670 | 1000 | PATIENT ROOM | NO REQUIREMENT FOR CONTINUOUS DIRECTIONAL CONTROL | 2 | 340 | NR | 1000 | 1000 | 1000 | 0
DUMMY | 1234 | 4444 | 10 | 4 | NR | - | 0 | 2970 | 4444 | PATIENT ROOM | NO REQUIREMENT FOR CONTINUOUS DIRECTIONAL CONTROL | 2 | 1490 | NR | 4445 | 4445 | 4445 | 0
DUMMY | 1234 | 1000 | 10 | 4 | NR | - | 0 | 670 | 1000 | PATIENT ROOM | NO REQUIREMENT FOR CONTINUOUS DIRECTIONAL CONTROL | 2 | 340 | NR | 1000 | 1000 | 1000 | 0
DUMMY | 1234 | 1000 | 10 | 4 | NR | - | 0 | 670 | 1000 | PATIENT ROOM | NO REQUIREMENT FOR CONTINUOUS DIRECTIONAL CONTROL | 2 | 340 | NR | 1000 | 1000 | 1000 | 0
DUMMY | 1234 | 1000 | 10 | 4 | NR | - | 0 | 670 | 1000 | PATIENT ROOM | NO REQUIREMENT FOR CONTINUOUS DIRECTIONAL CONTROL | 2 | 340 | NR | 1000 | 1000 | 1000 | 0
DUMMY | 1234 | 1000 | 10 | 4 | NR | - | 0 | 670 | 1000 | PATIENT ROOM | NO REQUIREMENT FOR CONTINUOUS DIRECTIONAL CONTROL | 2 | 340 | NR | 1000 | 1000 | 1000 | 0
DUMMY | 1234 | 1000 | 10 | 4 | NR | - | 0 | 670 | 1000 | PATIENT ROOM | NO REQUIREMENT FOR CONTINUOUS DIRECTIONAL CONTROL | 2 | 340 | NR | 1000 | 1000 | 1000 | 0
|  | 14011 | [10 empty] | 4740 |  | 14015 | 14015 | 14015 | 0