## Plumbing Code
NOTES
SPACE | HANDWASHING FIXTURE | SCRUB SINKS3 | TOILETS | BATHTUBS OR SHOWERS | SERVICE SINKS1 | CLINIC SINKS
Administration Lobby | [6 empty] | 1 | Each department or nursing unit shall be served by a housekeeping room equipped with a service sink. Departments may share service closets provided the departmental services are compatible. A dedicated housekeeping room shall be provided for the following services: Surgical/Catherization, ICU, NICU, nursery, dietary, renal dialysis and outpatient surgery.
Public Toilet - Male | 12 |  | 1 |  |  |  | 2 | Conventional spouts and controls on hot-and cold-water supplies are acceptable. Aerators are not permitted. Non-aerating laminar flow devices are permitted. Nourishment areas shall have a handwashing fixture in or immediately accessible from the nourishment area, in addition to a nourishment sink.
Public Toilet - Female | 12 |  | 1 |  |  |  | 3 | Scrub sinks shall be located outside of sterile procedure rooms. A minimum of two scrub sinks shall be provided in a surgical unit containing one operating room. Four scrub sinks shall be provided in surgical units containing two operating rooms. One additional scrub sink shall be provided per each additional operating room.
Airborne infection isolation room | 1 | [5 empty] | 4 | The scrub sink is in addition to the required number for surgeries. 5 The following fixtures shall be provided in airborne infection or protective environment rooms of hospitals only: a. Within an adjoining toilet room, a lavatory, a shower containing a seat or a space for a shower chair, and toilet equipped with bedpan flushing attachment with a vacuum breaker. b. A handwashing fixture within a separate anteroom.
Airborne infection isolation treatment/exam room | 1 | [5 empty] | 6 | The following fixtures shall be provided in isolation rooms of correctional treatment centers only: a. Within an adjoining toilet area, a handwashing fixture, a shower containing a seat or a space for a shower chair, and water closet equipped with bedpan flushing attachment with a vacuum breaker. b. A handwashing fixture within a separate anteroom.
Airborne infection isolation anteroom | 120 | [5 empty] | 7 | Includes burn center spaces, acute respiratory-care service spaces, and coronary-care service spaces.
Airborne infection isolation toilet room | 12 |  | 15 | 15 |  |  | 8 | A toilet room with handwashing fixture shall directly adjoin each procedure room.
Cardiac Catheterization procedure room |  | 14, 33 |  |  |  |  | 9 | One toilet with lavatory and one shower may serve two labor rooms.
Central Sterile Supply | 115 | [5 empty] | 10 | One additional scrub sink for each additional cesarean or delivery operating room.
Cesarean/Delivery Service Space | [6 empty] | 11 | Provide emergency eye-wash and shower.
Labor Rooms | 133 |  | 19 | 19 |  |  | 12 | Conveniently located for staff use.
Recovery Room | 133 |  |  |  |  | 1 | 13 | Fixtures serving individual patient rooms shall not be considered as meeting the required ratios for bedrooms not served by individual adjoining toilet or bathrooms.
Drug distribution station | 1 | [5 empty] | 14 | The clinic sink may be deleted if all bedrooms in the nursing unit are provided with adjoining toilets with bedpan flushing devices.
Cesarean operating room |  | 210, 33 |  |  |  |  | 15 | Conventional controls on hot-and cold-water supplies are acceptable. The water discharge points shall be 5 inches (127 millimeters) above the fixture rim. Aerators are not permitted. Non-aerating laminar flow devices are permitted.
Delivery room |  | 110, 33 |  |  |  |  | 16 | A minimum of one bathtub is required on each floor of an acute care or acute psychiatric hospital providing skilled nursing or intermediate care services. Special bathing facilities/gurney shower shall be provided at a minimum ratio of one per 100 beds for acute care facilities.
Staff lounge | [6 empty] | 17 | In a multiple-bed room, every bed position shall be within 20 feet (6 meters) of a hands-free handwashing fixture. Where an individual room concept is used, a handwashing fixture shall be provided within each infant care room.
Staff Toilet - Male | 12 |  | 1:1-15 |  |  |  | 18 | When three or more procedure rooms are provided.
Staff Toilet - Female | 12 |  | 1:1-15 |  |  |  | 19 | If a separate medicine room is provided, the room shall be equipped with a sink in addition to the nurses' station handwashing fixture. Hot-water supplies are optional.
LDR or LDRP room | 133 |  | 1 | 1 |  |  | 20 | Not required when there is a handwash fixture in the patient bed room.
Waiting area/room | [6 empty] | 21 | Handwashing fixtures may be deleted if room is used for storage and holding only.
Public Toilet - Male | 12 |  | 1 |  |  |  | 22 | If room is used only for temporary holding of soiled materials, clinic sink and work counter may be omitted. If the flushing-rim clinical sink is eliminated, facilities for cleaning bedpans shall be provided elsewhere.
Public Toilet - Female | 12 |  | 1 |  |  |  | 23 | Toilet shall be equipped with a bedpan flushing attachment.
Clinical Laboratory Service Space11 | 1 | [5 empty] | 24 | Optional services approved by the licensing agency shall comply with the applicable space requirements of OSHPD 1 and 2.
Dietetic Service Space |  |  |  |  | 1 |  | 25 | Shall be provided in each separate room where open medication is handled.
Kitchen | 133 | [5 empty] | 26 | Conveniently accessible throughout the unit.
Food serving area | 133 | [5 empty] | 27 | Includes rooms or areas within coronary and intensive-care units and postanethesia recovery rooms.
Food Preparation | 133 | [5 empty] | 28 | Modular toilet/sink combination units located within a privacy curtain may be used within individual patient space or private room. The toilet fixture shall be completely contained within cabinetry when not in use, and shall be enclosed when flushed. Bedpan washers shall not be permitted in patient bedrooms.
Dietary Staff Toilet - Male | 12 |  | 1:1-15 |  |  |  | 29 | In service spaces with procedure rooms that do not have dedicated patient toilets, provide a minimum of one patient toilet room with a separate handwashing fixture within the service space.
Dietary Staff Toilet - Female | 12 |  | 1:1-15 |  |  |  | 30 | Toilet room shall be accessible from the procedure room.
Emergency Service | 1 | [5 empty] | 31 | Scrub sink shall be located outside the staff entrance to the procedure room.
Open plan | 1:4 cubicles |  | 1 |  |  |  | 32 | Not used.
Observation unit(s) | 1:4 cubicles |  | 1:6 beds |  |  |  | 33 | Handwashing and scrub sink fixtures shall not be equipped with wrist or elbow blades but shall be equipped with sensor controls, or controls that do not involve contact with the upper extremities.
Trauma/Cardiac, Emergency surgery, Cystoscopy, Cast Room |  | 14,33 |  |  |  |  | 34 | If room is used only for temporary holding of soiled material, clinic sink and work counter may be omitted.
Intensive Care Units7 |  |  |  |  | 1 | 1 | 35 | A minimum of one separate accessible toilet room shall be provided for the use of patients. Patient toilet room(s) shall be equipped with a handwashing fixture and shall be accessible to the observation units(s) from the corridor. Reference CBC, Part 2, Section 1224.39.6.
Open plan | 1:3 beds33
Patient rooms28 | 133
Newborn Intensive Care Unit (NICU) | 1:4 bassinets17, 33 |  |  |  | 1 | 1
Treatment area/room | 1
Control station
Staff lounge
Staff Toilet - Male | 12 |  | 1:1-15
Staff Toilet- Female | 12 |  | 1:1-15
Employee dressing rooms and lockers
Staff Toilet - Male | 12 |  | 1:1-15
Staff Toilet - Female | 12 |  | 1:1-15
Exam and treatment rooms | 1
Housekeeping room1 |  |  |  |  | 1
Laboratories | 115
Laundry soiled linen, receiving, holding and sorting | 1
Medicine preparation room | 119
Morgue and Autopsy | 1
Nourishment area | 1+12
Nuclear Medicine room | 1
Mold room | 1
Patient room | 1
Patient toilet and bath facilities13 | 12 |  | 1:4 beds | 0.88611
Central bathing facility16 | 1 |  | 1 | 1
Special bathing facility16 |  |  |  | 1
Nurse Station27 | 1 |  | 112
Newborn/well baby nursery | 1:6 bassinets33
Workroom | 133
Gastrointestinal endoscopy procedure room | 133
Outpatient observation35 | 1 |  | 1
Pediatric and Adolescent Unit toilet room | 12,26 |  | 126
Pharmacy | 125
Staff Toilet - Male | 12 |  | 1:1-15
Staff Toilet - Female | 12 |  | 1:1-15
Compounding area for parenteral solutions | 133
Postanesthesia care units (PACU) | [5 empty] | 1
Open plan | 1:4 gurney
spaces33
Individual rooms | 133
Protective environment room | 133
Protective environment anteroom | 120,33
Protective environment toilet room | 12 |  | 15 | 15
Psychiatric unit patient room | 1 |  | 1
Radiological/Imaging Services Space | 1 |  | 129
Mammography | 1
Interventional imaging |  | 1
Ultrasound8 |  |  | 130
Angiography |  | 14,31
Fluoroscopy8 |  |  | 130
Staff Toilet18 - Male | 12 |  | 1:1-15
Staff Toilet18 - Female | 12 |  | 1:1-15
Rehabilitation Therapy Space
Training toilet |  |  | 1
Physical therapy service space | 1
Occupational therapy service space | 1
Speech pathology | 1
Infusion Therapy | 1
Renal Dialysis Service Space | 1:4 stations |  |  |  | 1
Bloodborne Infection Isolation Room | 1
Nurses' station | 1
Medication dispensing | 1
Home training room | 1
Repair room11 | 1 |  |  |  | 1
Dialysis patient toilet | 12 |  | 1
Staff lounge
Staff Toilet - Male | 1 |  | 1:1-15 | 1 shower
Staff Toilet - Female | 1 |  | 1:1-15 | 1 shower
Surgical Service Space |  | 233 |  |  | 1
Staff clothing change areas
Staff Toilet - Male | 12 |  | 1 | 1 shower
Staff Toilet - Female | 12 |  | 1 | 1 shower
Clean-up rooms | 1
Substerile area | 1
Anesthesia workroom | 1
Soiled workroom or soiled holding | 1 |  |  |  |  | 134
Cancer treatment/infusion therapy treatment | 1:4 stations
Utility/Work Room
Clean21 | 1
Soiled22 | 1 |  |  |  |  | 114
Patient beds [Skilled Nursing/Intermediate Care Facilities] [medical model] | 0.098611 |  | 1:06 | 1:20
Patient toilet and bath facilities13 [Correctional Treatment Center] | 0.098611 |  | 1:06 | 1:12
Airborne infection isolation anteroom6 [Correctional Treatment Center] | 16 |  | 16 | 16
Airborne infection isolation anteroom [Correctional Treatment Center] | 1
Protective environment room6 [Correctional Treatment Center] | 16 |  | 16 | 16
Protective environment anteroom [Correctional Treatment Center] | 1

## Sheet2
FIXTURE TAG | ROOM NAME | ROOM FUNCTION | HANDWASHING FIXTURE | Scrub Sink | Toilets | Bathtub or Shower | Service Sink | Clinic Sink