## Table 6-1 Rates
Standard 62.1 Outdoor Air Rates (Table 6-1) | [8 empty] | OVERRIDDEN
| IP |  | SI |  | Default Occupant Density | T24 Occ Minimum | T24 DCV Minimum | T24 DCV/Occ Standby
Occupancy Category | Rp (cfm/per) | Ra (cfm/ft2) | Rp (L/s-per) | Ra (L/s-m2) | #/1000 ft2 (#/100 m2) | T24 Occ Minimum CFM/sqft | T24 DCV Minimum CFM/sqft | T24 DCV/Occ Standby
Exam Room | 5 | 0.06 | 2.5 | 0.3 | 5 | 0.15 | 0 | 0.15 | *DON'T WANT TO MAKE AS AN OFFICE SPACE | ADDED CATEGORY
Imaging Room | 5 | 0.06 | 2.5 | 0.3 | 5 | 0.15 | 0 | 0.15 |  | ADDED CATEGORY
Waiting Room | 5 | 0.06 | 3.8 | 0.3 | 30 | #N/A | #N/A | #N/A | *CLASS F | ADDED CATEGORY
Nurse Station | 5 | 0.06 | 3.8 | 0.3 | 15 | 0.15 | 0 | 0.15 | *SAME AS OFFICE SPACE AND CLASS F | ADDED CATEGORY
Procedure Room | 5 | 0.15 | 5 | 0.3 | 5 | 0.15 | 0 | 0.15
Barracks sleeping areas | 5 | 0.06 | 2.5 | 0.3 | 20 | #N/A | #N/A | #N/A
Bars, cocktail lounges | 7.5 | 0.18 | 3.8 | 0.9 | 100 | #N/A | #N/A | #N/A
Beauty and nail salons | 20 | 0.12 | 10 | 0.6 | 25 | #N/A | #N/A | #N/A
Bedroom/living room | 5 | 0.06 | 2.5 | 0.3 | 10 | #N/A | #N/A | #N/A
Booking/waiting | 7.5 | 0.06 | 3.8 | 0.3 | 50 | #N/A | #N/A | #N/A
Bowling alley (seating) | 10 | 0.12 | 5 | 0.6 | 40 | #N/A | #N/A | #N/A
Break rooms | 5 | 0.06 | 2.5 | 0.6 | 25 | #N/A | #N/A | #N/A
Cafeteria/fast-food dining | 7.5 | 0.18 | 3.8 | 0.9 | 100 | #N/A | #N/A | #N/A
Cell | 5 | 0.12 | 2.5 | 0.6 | 25 | #N/A | #N/A | #N/A
Classrooms (age 9 -18) | 10 | 0.12 | 5 | 0.6 | 35 | #N/A | #N/A | #N/A
Classrooms (ages 5-8) | 10 | 0.12 | 5 | 0.6 | 25 | #N/A | #N/A | #N/A
Coffee stations | 5 | 0.06 | 2.5 | 0.3 | 20 | #N/A | #N/A | #N/A
Coin-operated laundries | 7.5 | 0.06 | 3.8 | 0.6 | 20 | #N/A | #N/A | #N/A
Common corridors | 0 | 0.06 | 0 | 0.3 |  | #N/A | #N/A | #N/A
Computer (not printing) | 5 | 0.06 | 2.5 | 0.3 | 4 | #N/A | #N/A | #N/A
Computer lab | 10 | 0.12 | 5 | 0.6 | 25 | #N/A | #N/A | #N/A
Conference/meeting | 5 | 0.06 | 2.5 | 0.3 | 50 | #N/A | #N/A | #N/A
Corridors | 0 | 0.06 | 0 | 0.3 | 0 | #N/A | #N/A | #N/A
Courtrooms | 5 | 0.06 | 2.5 | 0.3 | 70 | #N/A | #N/A | #N/A
Daycare (through age 4) | 10 | 0.18 | 5 | 0.9 | 25 | #N/A | #N/A | #N/A
Daycare sickroom | 10 | 0.18 | 5 | 0.9 | 25 | #N/A | #N/A | #N/A
Dayroom | 5 | 0.06 | 2.5 | 0.3 | 30 | #N/A | #N/A | #N/A
Disco/dance floors | 20 | 0.06 | 10 | 0.3 | 100 | #N/A | #N/A | #N/A
Dwelling unit | 5 | 0.06 | 2.5 | 0.3 | 2 | #N/A | #N/A | #N/A
Electrical equipment rooms | 0 | 0.06 | 0 | 0.3 | 0 | 0.15 | #N/A | #N/A
Elevator machine rooms | 0 | 0.12 | 0 | 0.6 | 0 | 0.15 | #N/A | #N/A
Gambling casinos | 7.5 | 0.18 | 3.8 | 0.9 | 120 | #N/A | #N/A | #N/A
Game arcades | 7.5 | 0.18 | 3.8 | 0.9 | 20 | #N/A | #N/A | #N/A
General manufacturing (excludes heavy industrial and process using chemicals) | 10 | 0.18 | 5 | 0.9 | 7 | #N/A | #N/A | #N/A
Guard stations | 5 | 0.06 | 2.5 | 0.3 | 15 | #N/A | #N/A | #N/A
Gym, sports arena (play area) | 0 | 0.3 | 0 | 1.5 | 30 | #N/A | #N/A | #N/A
Health club/aerobics room | 20 | 0.06 | 10 | 0.3 | 40 | #N/A | #N/A | #N/A
Health club/weight rooms | 20 | 0.06 | 10 | 0.3 | 10 | #N/A | #N/A | #N/A
Kitchen (cooking) | 7.5 | 0.12 | 3.8 | 0.6 | 20 | #N/A | #N/A | #N/A
Laundry rooms within dwelling units | 5 | 0.12 | 2.5 | 0.6 | 10 | #N/A | #N/A | #N/A
Laundry rooms, central | 5 | 0.12 | 2.5 | 0.6 | 10 | #N/A | #N/A | #N/A
Lecture/postsecondary classroom | 7.5 | 0.06 | 3.8 | 0.3 | 65 | #N/A | #N/A | #N/A
Lecture hall (fixed seats) | 7.5 | 0.06 | 3.8 | 0.3 | 150 | #N/A | #N/A | #N/A
Legislative chambers | 5 | 0.06 | 2.5 | 0.3 | 50 | #N/A | #N/A | #N/A
Libraries (reading rooms and stack areas) | 5 | 0.12 | 2.5 | 0.6 | 10 | #N/A | #N/A | #N/A
Lobbies | 5 | 0.06 | 2.5 | 0.3 | 150 | #N/A | #N/A | #N/A
Lobbies/pre-function | 7.5 | 0.06 | 3.8 | 0.3 | 30 | #N/A | #N/A | #N/A
Main entry lobbies | 5 | 0.06 | 2.5 | 0.3 | 10 | #N/A | #N/A | #N/A
Mall common areas | 7.5 | 0.06 | 3.8 | 0.3 | 40 | #N/A | #N/A | #N/A
Media center | 10 | 0.12 | 5 | 0.6 | 25 | #N/A | #N/A | #N/A
Multipurpose assembly | 5 | 0.06 | 2.5 | 0.3 | 120 | #N/A | #N/A | #N/A
Multiuse assembly | 7.5 | 0.06 | 3.8 | 0.3 | 100 | #N/A | #N/A | #N/A
Museums (children’s) | 7.5 | 0.12 | 3.8 | 0.6 | 40 | #N/A | #N/A | #N/A
Museums/galleries | 7.5 | 0.06 | 3.8 | 0.3 | 40 | #N/A | #N/A | #N/A
Music/theater/dance | 10 | 0.06 | 5 | 0.3 | 35 | #N/A | #N/A | #N/A
Occupiable storage rooms for liquids or gels | 5 | 0.12 | 2.5 | 0.6 | 2 | #N/A | #N/A | #N/A
Storage rooms | 5 | 0.06 | 2.5 | 0.3 | 2 | #N/A | #N/A | #N/A
Office space | 5 | 0.06 | 2.5 | 0.3 | 5 | #N/A | #N/A | #N/A
Pet shops (animal areas) | 7.5 | 0.18 | 3.8 | 0.9 | 10 | #N/A | #N/A | #N/A
Pharmacy (prep. area) | 5 | 0.18 | 2.5 | 0.9 | 10 | #N/A | #N/A | #N/A
Photo studios | 5 | 0.12 | 2.5 | 0.6 | 10 | #N/A | #N/A | #N/A
Places of religious worship | 5 | 0.06 | 2.5 | 0.3 | 120 | #N/A | #N/A | #N/A
Reception areas | 5 | 0.06 | 2.5 | 0.3 | 30 | #N/A | #N/A | #N/A
Restaurant dining rooms | 7.5 | 0.18 | 3.8 | 0.9 | 70 | #N/A | #N/A | #N/A
Sales (except as below) | 7.5 | 0.12 | 3.8 | 0.6 | 15 | #N/A | #N/A | #N/A
Science laboratories | 10 | 0.18 | 5 | 0.9 | 25 | #N/A | #N/A | #N/A
Shipping/receiving |  | 0.12 | 5 | 0.6 | 0 | #N/A | #N/A | #N/A
Sorting, packing, light assembly | 7.5 | 0.12 | 3.8 | 0.6 | 7 | #N/A | #N/A | #N/A
Spectator areas | 7.5 | 0.06 | 3.8 | 0.3 | 150 | #N/A | #N/A | #N/A
Gym, sports arena (play area) | 0 | 0.3 | 0 | 1.5 | 0 | #N/A | #N/A | #N/A
Stages, studios | 10 | 0.06 | 5 | 0.3 | 70 | #N/A | #N/A | #N/A
Storage rooms | 0 | 0.12 | 0 | 0.6 | 0 | #N/A | #N/A | #N/A
Supermarket | 7.5 | 0.06 | 3.8 | 0.3 | 8 | #N/A | #N/A | #N/A
Swimming | 0 | 0.48 | 0 | 2.4 | 0 | 0.15 | 0 | #REF!
Telephone closets | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A
Telephone/data entry | 5 | 0.06 | 2.5 | 0.3 | 60 | #N/A | #N/A | #N/A
Transportation waiting | 7.5 | 0.06 | 3.8 | 0.3 | 100 | #N/A | #N/A | #N/A
University/college laboratories | 10 | 0.18 | 5 | 0.9 | 25 | #N/A | #N/A | #N/A
Warehouses | 0 | 0.06 | 5 | 0.3 | 0 | #N/A | #N/A | #N/A
Wood/metal shop | 10 | 0.18 | 5 | 0.9 | 20 | #N/A | #N/A | #N/A

## T-24 TAble 120.1-A
Occupancy Category | Total Outdoor Air Rate1 Rt (cfm/ft2) | Min Ventilation Air Rate for DCV2 Ra (cfm/ft2) | Air Class | OS
Educational Facilities - Daycare (through age 4) | 0.21 | 0.15 | 2
Educational Facilities - Daycare sickroom | 0.15 |  | 3
Educational Facilities - Classrooms (ages 5-8) | 0.38 | 0.15 | 1
Educational Facilities - Classrooms (age 9 -18) | 0.38 | 0.15 | 1
Educational Facilities - Lecture/postsecondary classroom | 0.38 | 0.15 | 1 | YES
Educational Facilities - Lecture hall (fixed seats) | 0 | 0.15 | 1 | YES
Educational Facilities - Art classroom | 0.15 |  | 2
Educational Facilities - Science laboratories | 0.15 |  | 2
Educational Facilities - University/college laboratories | 0.15 |  | 2
Educational Facilities - University/college laboratories | 0.15 |  | 2
Educational Facilities - Computer lab | 0.15 |  | 1
Educational Facilities - Media center | 0.15 |  | 1
Educational Facilities - Music/theater/dance | 1.07 | 0.15 | 1 | YES
Educational Facilities - Multiuse assembly | 0.5 | 0.15 | 1 | YES
Food and Beverage Service - Restaurant dining rooms | 0.5 | 0.15 | 2
Food and Beverage Service - Cafeteria/fast-food dining | 0.5 | 0.15 | 2
Food and Beverage Service - Bars, cocktail lounges | 0.5 | 0.2 | 2
Food and Beverage Service - Kitchen (cooking) | 0.15 |  | 2
General - Break rooms (not office) | 0.5 | 0.15 | 1 | YES
General - Coffee Stations | 0.5 | 0.15 | 1 | YES
General - Conference/meeting | 0.5 | 0.15 | 1 | YES
General - Corridors | 0.15 |  | 1 | YES
General - Occupiable storage rooms for liquids or gels | 0.15 |  | 2 | YES
Hotels, Motels, Resorts, Dormitories - Bedroom/living room | 0.15 |  | 1 | YES
Hotels, Motels, Resorts, Dormitories - Barracks sleeping areas | 0.15 |  | 1 | YES
Hotels, Motels, Resorts, Dormitories - Laundry rooms, central | 0.15 |  | 2
Hotels, Motels, Resorts, Dormitories - Laundry rooms within dwelling units | 0.15 |  | 1
Hotels, Motels, Resorts, Dormitories - Lobbies/pre-function | 0.5 | 0.15 | 1 | YES
Hotels, Motels, Resorts, Dormitories - Multipurpose assembly | 0.5 |  | 1 | YES
Office Buildings - Break rooms | 0.5 | 0.15 | 1
Office Buildings - Main entry lobbies | 0.5 | 0.15 | 1 | YES
Office Buildings - storage rooms | 0.15 |  | 1
Office Buildings - Office space | 0.15 |  | 1 | YES
Office Buildings - Reception areas | 0.15 |  | 1 | YES
Office Buildings - Telephone/data entry | 0.15 |  | 1 | YES
Miscellaneous Spaces - Bank vaults/safe deposit | 0.15 |  | 2 | YES
Miscellaneous Spaces - Banks or bank lobbies | 0.15 |  | 1 | YES
Miscellaneous Spaces - Computer (not printing) | 0.15 |  | 1 | YES
Miscellaneous Spaces - Freezer and refrigerated spaces (<50oF) | - |  | 2
Miscellaneous Spaces - General manufacturing (excludes heavy industrial and process using chemicals) | 0.15 |  | 3
Miscellaneous Spaces - Pharmacy (prep. Area) | 0.15 |  | 2
Miscellaneous Spaces - Photo studios | 0.15 |  | 1
Miscellaneous Spaces - Shipping/receiving | 0.15 |  | 2
Miscellaneous Spaces - Sorting, packing, light assembly | 0.15 |  | 2
Miscellaneous Spaces - Telephone closets | 0.15 |  | 1
Miscellaneous Spaces - Transportation waiting | 0.5 | 0.15 | 1 | YES
Miscellaneous Spaces - Warehouses | 0.15 |  | 2
Miscellaneous Spaces - All others | 0.15 |  | 2
Public Assembly Spaces - Auditorium seating area | 1.07 | 0.15 | 1 | YES
Public Assembly Spaces - Places of religious worship | 1.07 | 0.15 | 1 | YES
Public Assembly Spaces - Courtrooms | 0.19 | 0.15 | 1 | YES
Public Assembly Spaces - Legislative chambers | 0.19 | 0.15 | 1 | YES
Public Assembly Spaces - Libraries (reading rooms and stack areas) | 0.15 |  | 1
Public Assembly Spaces - Lobbies | 0.5 | 0.15 | 1 | YES
Public Assembly Spaces - Museums (children’s) | 0.25 | 0.15 | 1
Public Assembly Spaces - Museums/galleries | 0.25 | 0.15 | 11 | YES
Residential - Common corridors | 0 | 0
Retail - Sales (except as below) | 0.25 | 0.2 | 2
Retail - Mall common areas | 0.25 | 0.15 | 1 | YES
Retail - Barbershop | 0.4 |  | 2
Retail - Beauty and nail salons | 0.4 |  | 2
Retail - Pet shops (animal areas) | 0.25 | 0.15 | 2
Retail - Supermarket | 0.25 | 0.2 | 1 | YES
Retail - Coin-operated laundries | 0.3 |  | 2
Sports and Entertainment - Gym, sports arena (play area) | 0.5 | 0.15 | 2
Sports and Entertainment - Spectator areas | 0.5 | 0.15 | 1 | YES
Sports and Entertainment - Swimming (pool) | 0.15 |  | 2
Sports and Entertainment - Swimming (deck) | 0.5 | 0.15 | 2
Sports and Entertainment - Disco/dance floors | 1.5 | 0.15 | 2 | YES
Sports and Entertainment - Health club/aerobics room | 0.15 |  | 2
Sports and Entertainment - Health club/weight rooms | 0.15 |  | 2
Sports and Entertainment - Bowling alley (seating) | 1.07 | 0.15 | 1
Sports and Entertainment - Gambling casinos | 0.68 | 0.15 | 1
Sports and Entertainment - Game arcades | 0.68 | 0.15 | 1
Sports and Entertainment - Stages, studios | 0.5 | 0.15 | 1 | YES

## RTU 1-1
IP
| VAV-1-1-1 | VAV-1-1-2 | VAV-1-1-3 | VAV-1-2-1 | VAV-1-2-2 | VAV-1-2-3 | VAV-1-2-4 | VAV-1-2-5 | VAV-1-3-1 | VAV-1-3-2 | VAV-1-3-3 | VAV-1-3-4 | VAV-1-3-5 | VAV-1-3-6 | VAV-1-3-7 | VAV-1-4-1 | VAV-1-4-2 | VAV-1-4-3 | VAV-1-4-4 | VAV-1-5-1 | VAV-1-5-2 | VAV-1-5-3 |  |  |  |  | new zone | Totals/averages
New zone ID
Room Type | Sales (except as below) | Pharmacy (prep. area) | Storage rooms | Exam Room | Nurse Station | Nurse Station | Nurse Station | Conference/meeting | Main entry lobbies | Storage rooms | Break rooms | Nurse Station | Office space | Nurse Station | Nurse Station | Laundry rooms, central | Electrical equipment rooms | Nurse Station | Office space | Waiting Room | Waiting Room | Exam Room | Office space | Office space | Office space | Office space | Office space
Area | 524 | 763 | 169 | 692.1 | 313.9 | 451 | 651.1 | 390 | 641.1 | 561.2 | 387 | 295.2 | 763.4 | 190 | 292 | 400 | 679 | 502 | 555.5 | 672 | 228.7 | 181.5 |  |  |  |  | 10302.7 | sq. ft.
People | 7.86 | 7.63 | 0.338 | 3.4605 | 4.7085 | 6.765 | 9.7665 | 19.5 | 6.411 | 1.1224 | 9.675 | 4.428 | 3.817 | 2.85 | 4.38 | 4 | 0 | 7.53 | 2.7775 | 20.16 | 6.861 | 0.9075 | 0 | 0 | 0 | 0 | 134.9479 | People
VareaMin T-24 | #N/A | #N/A | #N/A | 103.815 | 47.085 | 67.65 | 97.665 | #N/A | #N/A | #N/A | #N/A | 44.28 | #N/A | 28.5 | 43.8 | #N/A | 101.85 | 75.3 | #N/A | #N/A | #N/A | 27.225 | #N/A | #N/A | #N/A | #N/A | 637.17
Voccmin T-24 DCV | #N/A | #N/A | #N/A | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | 0 | 0 | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | 0
VoccMin OccStandby | #N/A | #N/A | #N/A | 103.815 | 47.085 | 67.65 | 97.665 | #N/A | #N/A | #N/A | #N/A | 44.28 | #N/A | 28.5 | 43.8 | #N/A | #N/A | 75.3 | #N/A | #N/A | #N/A | 27.225 | #N/A | #N/A | #N/A | #N/A | 535.32
OccSensor Req | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | RTU 1-1 | ABSMIN | 535.32
co2 REQ? | NO | NO | NO | NO | NO | NO | NO | YES | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | YES | YES | NO | NO | NO |  | DESMINOA | 637.17

## RTU 2-X
IP
| VAV-2-1-1 | VAV-2-1-2 | VAV-2-1-3 | VAV-2-2-1 | VAV-2-2-2 | VAV-2-2-3 | VAV-2-2-4 | VAV-2-2-5 | VAV-2-2-6 | VAV-2-3-1 | VAV-2-3-2 | VAV-2-3-3 | VAV-2-3-4 | VAV-2-3-5 | VAV-2-3-6 | VAV-2-3-7 | VAV-2-4-1 | VAV-2-4-2 | VAV-2-4-3 | VAV-2-4-4 | VAV-2-4-5 | VAV-2-4-6 | VAV-2-4-7 | VAV-2-4-8 | VAV-2-4-9 | VAV-2-5-1 | VAV-2-5-2 | VAV-2-5-3 | VAV-2-5-4 | VAV-2-5-5 | VAV-2-5-6 | VAV-2-5-7 | new zone | Totals/averages
New zone ID
Room Type | Corridors | Exam Room | Exam Room | Exam Room | Exam Room | Exam Room | Nurse Station | Waiting Room | Exam Room | Exam Room | Exam Room | Exam Room | Exam Room | Corridors | Nurse Station | Conference/meeting | Exam Room | Exam Room | Exam Room | Exam Room | Exam Room | Exam Room | Corridors | Exam Room | Nurse Station | Main entry lobbies | Storage rooms | Waiting Room | Corridors | Waiting Room | Exam Room | Waiting Room | Office space
Area | 351 | 105 | 400 | 296.8 | 379.8 | 382.7 | 712.8 | 361.8 | 627.4 | 410 | 200 | 100.8 | 105.3 | 220 | 215 | 312 | 109 | 297 | 297 | 198.8 | 100.8 | 110 | 200 | 123.8 | 325 | 440 | 108.8 | 496 | 987 | 131 | 591.4 | 200 | 9896
People | 0 | 0.525 | 2 | 1.484 | 1.899 | 1.9135 | 10.692 | 10.854 | 3.137 | 2.05 | 1 | 0.504 | 0.5265 | 0 | 3.225 | 15.6 | 0.545 | 1.485 | 1.485 | 0.994 | 0.504 | 0.55 | 0 | 0.619 | 4.875 | 4.4 | 0.2176 | 14.88 | 0 | 3.93 | 2.957 | 6 | 98.8516
VareaMin T-24 | #N/A | 15.75 | 60 | 44.52 | 56.97 | 57.405 | 106.92 | #N/A | 94.11 | 61.5 | 30 | 15.12 | 15.795 | #N/A | 32.25 | #N/A | 16.35 | 44.55 | 44.55 | 29.82 | 15.12 | 16.5 | #N/A | 18.57 | 48.75 | #N/A | #N/A | #N/A | #N/A | #N/A | 88.71 | #N/A | 913.26
Voccmin T-24 DCV | #N/A | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | 0 | 0 | 0 | 0 | 0 | #N/A | 0 | #N/A | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | 0
VoccMin OccStandby | #N/A | 15.75 | 60 | 44.52 | 56.97 | 57.405 | 106.92 | #N/A | 94.11 | 61.5 | 30 | 15.12 | 15.795 | #N/A | 32.25 | #N/A | 16.35 | 44.55 | 44.55 | 29.82 | 15.12 | 16.5 | #N/A | 18.57 | 48.75 | #N/A | #N/A | #N/A | #N/A | #N/A | 88.71 | #N/A | 913.26
OccSensor Req | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
co2 REQ? | NO | NO | NO | NO | NO | NO | NO | YES | NO | NO | NO | NO | NO | NO | NO | YES | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | YES | NO | YES | NO | YES
[31 empty] | RTU 2-X | ABSMIN | 913.26
[32 empty] | DESMINOA | 913.26

## AC-3
IP
| VAV-3-1 | VAV-3-2 | VAV-3-3 | VAV-3-4 | VAV-3-5 | VAV-3-6 | VAV-3-7 | VAV-3-8 | VAV-3-9 | VAV-3-10 | VAV-3-11 | VAV-3-12 | VAV-3-13 | VAV-3-14 | VAV-3-15 | VAV-3-16 | VAV-3-17 | VAV-3-18 |  |  | new zone | Totals/averages
| OEXPO | HALLW | LOBBY | GROUP | WTAGN | OGENL | GROUP | OEXPO | HALLW | OEXPO | OEXPO | WSGEN | OGENL | OEXPO | OGENL | OEXPO | OEXPO | HALLW |  |  | New zone ID
Room Type | Office space | Corridors | Lobbies/pre-function | Conference/meeting | Waiting Room | Office space | Conference/meeting | Office space | Corridors | Office space | Office space | Nurse Station | Office space | Office space | Office space | Office space | Office space | Corridors | Exam Room | Office space
Area | 1122 | 1492 | 1440 | 528 | 1102 | 184 | 524 | 1129 | 969 | 1136 | 224 | 897 | 246 | 1090 | 329 | 674 | 667 | 942 |  |  | 14695 | SQ.FT
People | 5.61 | 0 | 43.2 | 26.4 | 33.06 | 0.92 | 26.2 | 5.645 | 0 | 5.68 | 1.12 | 13.455 | 1.23 | 5.45 | 1.645 | 3.37 | 3.335 | 0 | 0 | 0 | 176.32 | PEOPLE
VareaMin T-24 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 134.55 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A
Voccmin T-24 DCV | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A
VoccMin OccStandby | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 134.55 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A
OccSensor Req | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
co2 REQ? | NO | NO | YES | YES | YES | NO | YES | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO
[19 empty] | AC-3 | ABSMIN | #N/A
[20 empty] | DESMINOA | #N/A

## AUTOCAD
EXISTING TERMINAL UNIT SCHEDULE
TAG | PARENT | PRIMARY OCCUPANCY | AS-BUILT CAPACITIES (SEE NOTE 1) |  |  | GUIDELINES 36 CONTROLS SETPOINTS
|  |  | INLET DIAMETER (IN) | MAX AIRFLOW (CFM) | REHEAT COIL | VCOOL-MAX CFM | VMIN CFM | VHEAT-MAX CFM | MAX dt F | VHEAT-MIN CFM | VOCC-MIN CFM | VAREA-MIN CFM | CO2 REQUIRED | CO2 SETPOINT | OCC SENSOR REQUIRED
VAV-1-1-1 |  | 0 | [8 empty] | #N/A | #N/A | NO | N/A | #N/A
VAV-1-1-2 |  | 0 | [8 empty] | #N/A | #N/A | NO | N/A | #N/A
VAV-1-1-3 |  | 0 | [8 empty] | #N/A | #N/A | NO | N/A | #N/A
VAV-1-2-1 |  | 0 | [8 empty] | 0 | 103.815 | NO | N/A | #N/A
VAV-1-2-2 |  | 0 | [8 empty] | 0 | 47.085 | NO | N/A | #N/A
VAV-1-2-3 |  | 0 | [8 empty] | 0 | 67.65 | NO | N/A | #N/A
VAV-1-2-4 |  | 0 | [8 empty] | 0 | 97.665 | NO | N/A | #N/A
VAV-1-2-5 |  | 0 | [8 empty] | #N/A | #N/A | YES | 600 | #N/A
VAV-1-3-1 |  | 0 | [8 empty] | #N/A | #N/A | NO | N/A | #N/A
VAV-1-3-2 |  | 0 | [8 empty] | #N/A | #N/A | NO | N/A | #N/A
VAV-1-3-3 |  | 0 | [8 empty] | #N/A | #N/A | NO | N/A | #N/A
VAV-1-3-4 |  | 0 | [8 empty] | 0 | 44.28 | NO | N/A | #N/A
VAV-1-3-5 |  | 0 | [8 empty] | #N/A | #N/A | NO | N/A | #N/A
VAV-1-3-6 |  | 0 | [8 empty] | 0 | 28.5 | NO | N/A | #N/A
VAV-1-3-7 |  | 0 | [8 empty] | 0 | 43.8 | NO | N/A | #N/A
VAV-1-4-1 |  | 0 | [8 empty] | #N/A | #N/A | NO | N/A | #N/A
VAV-1-4-2 |  | 0 | [8 empty] | #N/A | 101.85 | NO | N/A | #N/A
VAV-1-4-3 |  | 0 | [8 empty] | 0 | 75.3 | NO | N/A | #N/A
VAV-1-4-4 |  | 0 | [8 empty] | #N/A | #N/A | NO | N/A | #N/A
VAV-1-5-1 |  | 0 | [8 empty] | #N/A | #N/A | YES | 600 | #N/A
VAV-1-5-2 |  | 0 | [8 empty] | #N/A | #N/A | YES | 600 | #N/A
VAV-1-5-3 |  | 0 | [8 empty] | 0 | 27.225 | NO | N/A | #N/A
0 |  | #N/A | [8 empty] | #N/A | #N/A | #N/A | #N/A | #N/A
0 |  | #N/A | [8 empty] | #N/A | #N/A | #N/A | #N/A | #N/A
VAV-2-1-1 |  | 0 | [8 empty] | #N/A | #N/A | NO | N/A | #N/A
VAV-2-1-2 |  | 0 | [8 empty] | 0 | 15.75 | NO | N/A | #N/A
VAV-2-1-3 |  | 0 | [8 empty] | 0 | 60 | NO | N/A | #N/A
VAV-2-2-1 |  | 0 | [8 empty] | 0 | 44.52 | NO | N/A | #N/A
VAV-2-2-2 |  | 0 | [8 empty] | 0 | 56.97 | NO | N/A | #N/A
VAV-2-2-3 |  | 0 | [8 empty] | 0 | 57.405 | NO | N/A | #N/A
VAV-2-2-4 |  | 0 | [8 empty] | 0 | 106.92 | NO | N/A | #N/A
VAV-2-2-5 |  | 0 | [8 empty] | #N/A | #N/A | YES | 600 | #N/A
VAV-2-2-6 |  | 0 | [8 empty] | 0 | 94.11 | NO | N/A | #N/A
VAV-2-3-1 |  | 0 | [8 empty] | 0 | 61.5 | NO | N/A | #N/A
VAV-2-3-2 |  | 0 | [8 empty] | 0 | 30 | NO | N/A | #N/A
VAV-2-3-3 |  | 0 | [8 empty] | 0 | 15.12 | NO | N/A | #N/A
VAV-2-3-4 |  | 0 | [8 empty] | 0 | 15.795 | NO | N/A | #N/A
VAV-2-3-5 |  | 0 | [8 empty] | #N/A | #N/A | NO | N/A | #N/A
VAV-2-3-6 |  | 0 | [8 empty] | 0 | 32.25 | NO | N/A | #N/A
VAV-2-3-7 |  | 0 | [8 empty] | #N/A | #N/A | YES | 600 | #N/A
VAV-2-4-1 |  | 0 | [8 empty] | 0 | 16.35 | NO | N/A | #N/A
VAV-2-4-2 |  | 0 | [8 empty] | 0 | 44.55 | NO | N/A | #N/A
VAV-2-4-3 |  | 0 | [8 empty] | 0 | 44.55 | NO | N/A | #N/A
VAV-2-4-4 |  | 0 | [8 empty] | 0 | 29.82 | NO | N/A | #N/A
VAV-2-4-5 |  | 0 | [8 empty] | 0 | 15.12 | NO | N/A | #N/A
VAV-2-4-6 |  | 0 | [8 empty] | 0 | 16.5 | NO | N/A | #N/A
VAV-2-4-7 |  | 0 | [8 empty] | #N/A | #N/A | NO | N/A | #N/A
VAV-2-4-8 |  | 0 | [8 empty] | 0 | 18.57 | NO | N/A | #N/A
VAV-2-4-9 |  | 0 | [8 empty] | 0 | 48.75 | NO | N/A | #N/A
VAV-2-5-1 |  | 0 | [8 empty] | #N/A | #N/A | NO | N/A | #N/A
VAV-2-5-2 |  | 0 | [8 empty] | #N/A | #N/A | NO | N/A | #N/A
VAV-2-5-3 |  | 0 | [8 empty] | #N/A | #N/A | YES | 600 | #N/A
VAV-2-5-4 |  | 0 | [8 empty] | #N/A | #N/A | NO | N/A | #N/A
VAV-2-5-5 |  | 0 | [8 empty] | #N/A | #N/A | YES | 600 | #N/A
VAV-2-5-6 |  | 0 | [8 empty] | 0 | 88.71 | NO | N/A | #N/A
VAV-2-5-7 |  | 0 | [8 empty] | #N/A | #N/A | YES | 600 | #N/A
|  | #N/A | [8 empty] | #N/A | #N/A | #N/A | #N/A | #N/A
|  | #N/A | [8 empty] | #N/A | #N/A | #N/A | #N/A | #N/A
|  | #N/A | [8 empty] | #N/A | #N/A | #N/A | #N/A | #N/A
|  | #N/A | [8 empty] | #N/A | #N/A | #N/A | #N/A | #N/A
|  | #N/A | [8 empty] | #N/A | #N/A | #N/A | #N/A | #N/A
|  | #N/A | [8 empty] | #N/A | #N/A | #N/A | #N/A | #N/A
|  | #N/A | [8 empty] | #N/A | #N/A | #N/A | #N/A | #N/A
|  | #N/A | [8 empty] | #N/A | #N/A | #N/A | #N/A | #N/A
|  | #N/A | [8 empty] | #N/A | #N/A | #N/A | #N/A | #N/A
|  | #N/A | [8 empty] | #N/A | #N/A | #N/A | #N/A | #N/A
|  | #N/A | [8 empty] | #N/A | #N/A | #N/A | #N/A | #N/A
|  | #N/A | [8 empty] | #N/A | #N/A | #N/A | #N/A | #N/A