## Sheet1
Design Requirements Table
System | Compliance Rrequirement | Related to | Setpoints to be defined | Notes
General | All | Zone | Zone temperature | Based on zone types such as VAV, mech room, telecom room etc. Must show the occupied and unoccupied setpoint
General | Title 24 | Outside Air | Vocc_min, Varea_min, OS | Basically area based, occupancy based and where occupancy standby mode is allowed.
General | ASHRAE 90.1 | Outside Air | Vbz, Ez, OS | If our table from excel is included on the drawigns, these values are defined.
General | Title 24 | Outside Air | CO2 Setpoint | CO2 setpoint for all occupancy types is 1000 ppm
General | ASHRAE 90.1 | Outside Air | CO2 Setpoint | Add a note somewhere to provide per ASHRAE standard 62.1
Multizone System

## Points_Lists
VAV TERMINAL UNIT WITH REHEAT
Required | Description | Device | Type
R | VAV box damper position | Modulating actuator | AO
R | VAV box damper position | Floating actuator | DO
R | Discharge airflow | Differential pressure (DP) transducer connected to flow sensor | AI
R | Zone temperature | Room temperature sensor | AI
Zone Tstat | Local override | Zone thermostat override switch | DI
DCV | Occupancy sensor | Occupancy sensor | DI
Window DCV | Window switch | Window switch | DI
Zone Tstat | Zone temperature setpoint adjustment | Zone thermostat adjustment | AI
CO2 DCV | Zone CO2 level | Room CO2 sensor | AI
R | VAV box damper position | Modulating actuator | AO
R | VAV box damper position | Floating actuator | DO
Heating coil | Heating signal | Modulating valve | AO
Heating coil | Heating signal | Floating actuator | DO
Heating coil | Heating signal | Modulating electric heating coil | DO
Heating coil | Discharge air temperature (DAT) | Duct temperature sensor (probe or averaging at designer’s discretion) | AI
MULTIZONE AHU
Required | Description | Device | Type
R | Supply fan start/stop | Connect to VFD Run | DO
High Static Reset | Supply fan high static alarm reset | Dry contact to 120 or 24 V control circuit | DO
R | Supply fan speed | Connect to VFD Speed | AO
R | Supply fan status | Connect to VFD Status | DI
R | Supply air temperature | Duct temperature sensor (probe or averaging at designer’s discretion) | AI
R | Duct static pressure (DSP) | DP transducer down duct | AI
Prefilter | Filter pressure drop | DP transducer across filter | AI
Intermidiate Filter | Filter pressure drop | DP transducer across filter | AI
Final Filter | Filter pressure drop | DP transducer across filter | AI
R | Heating coil supply air temperature | Averaging temperature sensor | AI
Economizer | Economizer outdoor air damper | Modulating actuator | AO
R | Return air damper | Modulating actuator | AO
R | Outdoor air temperature | Temperature sensor at outdoor air intake | AI
R | Mixed air temperature | Averaging temperature sensor | AI
R | Return air temperature | Duct temperature sensor | AI
R | Cooling signal | Modulating CHW valve | AO
Preheating coil | Heating signal | Modulating HW valve | AO
Electric Preheating coil | Heating signal | Modulating electric heating coil | AO
Reheating coil | Heating signal | Modulating HW valve | AO
Electric Reheating coil | Heating signal | Modulating electric heating coil | AO
Common Econ | Outdoor airflow | Airflow measurement station (AFMS) | AI
Split Econ | Minimum outdoor air damper | Modulating actuator | AO
Split Econ | Minimum outdoor airflow | Airflow measurement station | AI
Relief Damper | Relief damper open/close | Modulating actuator | AO
Relief Damper | Building static pressure | DP transducer between representative space and outdoors | AI
Relief Fan | Relief-fan start/stop | Connect to VFD Run | DO
Relief Fan | Relief-fan status | Connect to VFD Status | DI
Relief Fan | Relief-fan speed | Connect to VFD Speed | AO
Relief Fan | Relief damper open/close | Two position actuator | DO
Relief Fan | Building static pressure | DP transducer between representative space and outdoors | AI
Retrun Fan | Return fan start/stop | Connect to VFD Run | DO
Retrun Fan | Return-fan status | Connect to VFD Status | DI
Retrun Fan | Return-fan high-static alarm reset | Dry contact to 120V or 24V control circuit | DO
Retrun Fan | Return-fan speed | Connect to VFD Speed | AO
Return Fan Airflow Tracking | Supply airflow (if airflow tracking logic used) | Airflow measurement station at supply fan (or sum of VAV zones) | AI
Return Fan Airflow Tracking | Return airflow (if airflow tracking logic used) | Airflow measurement station at return fan | AI
Return Fan Building Static | Return-fan discharge static pressure | DP transducer at fan | AI
Return Fan | Exhaust damper | Modulating actuator | AO
Return Fan Building Static | Building static pressure | DP transducer between representative space and outdoors | AI