## Setpoints_Requirements
Design Requirements Table
System | Compliance Rrequirement | Related to | Setpoints to be defined | Notes
General | All | Zone | Zone temperature | Based on zone types such as VAV, mech room, telecom room etc. Must show the occupied and unoccupied setpoint
General | Title 24 | Outside Air | Vocc_min, Varea_min, OS | Basically area based, occupancy based and where occupancy standby mode is allowed.
General | ASHRAE 90.1 | Outside Air | Vbz, Ez, OS | If our table from excel is included on the drawigns, these values are defined.
General | Title 24 | Outside Air | CO2 Setpoint | CO2 setpoint for all occupancy types is 1000 ppm
General | ASHRAE 90.1 | Outside Air | CO2 Setpoint | Add a note somewhere to provide per ASHRAE standard 62.1
VAV Terminal Unit | All

## Points_Lists
VAV TERMINAL UNIT WITH REHEAT
Required | Description | Device | Type
CO2 DCV | Zone CO2 level | Room CO2 sensor | AI
Heating coil | Heating signal | Modulating valve | AO
Heating coil | Heating signal | Floating actuator | DO
Heating coil | Heating signal | Modulating electric heating coil | DO
Heating coil | Discharge air temperature (DAT) | Duct temperature sensor (probe or averaging at designer’s discretion) | AI
Occupancy DCV | Occupancy sensor | Occupancy sensor | DI
R | VAV box damper position | Modulating actuator | AO
R | VAV box damper position | Floating actuator | DO
R | Discharge airflow | Differential pressure (DP) transducer connected to flow sensor | AI
R | Zone temperature | Room temperature sensor | AI
R | VAV box damper position | Modulating actuator | AO
R | VAV box damper position | Floating actuator | DO
Window DCV | Window switch | Window switch | DI
Zone Tstat | Local override | Zone thermostat override switch | DI
Zone Tstat | Zone temperature setpoint adjustment | Zone thermostat adjustment | AI
MULTIZONE AHU
Required | Description | Device | Type
Common Econ | Outdoor airflow | Airflow measurement station (AFMS) | AI
Economizer | Economizer outdoor air damper | Modulating actuator | AO
Electric Preheating coil | Heating signal | Modulating electric heating coil | AO
Electric Reheating coil | Heating signal | Modulating electric heating coil | AO
Final Filter | Filter pressure drop | DP transducer across filter | AI
High Static Reset | Supply fan high static alarm reset | Dry contact to 120 or 24 V control circuit | DO
Intermidiate Filter | Filter pressure drop | DP transducer across filter | AI
Prefilter | Filter pressure drop | DP transducer across filter | AI
Preheating coil | Heating signal | Modulating HW valve | AO
R | Supply fan start/stop | Connect to VFD Run | DO
R | Supply fan speed | Connect to VFD Speed | AO
R | Supply fan status | Connect to VFD Status | DI
R | Supply air temperature | Duct temperature sensor (probe or averaging at designer’s discretion) | AI
R | Duct static pressure (DSP) | DP transducer down duct | AI
R | Heating coil supply air temperature | Averaging temperature sensor | AI
R | Return air damper | Modulating actuator | AO
R | Outdoor air temperature | Temperature sensor at outdoor air intake | AI
R | Mixed air temperature | Averaging temperature sensor | AI
R | Return air temperature | Duct temperature sensor | AI
R | Cooling signal | Modulating CHW valve | AO
Reheating coil | Heating signal | Modulating HW valve | AO
Relief Damper | Relief damper open/close | Modulating actuator | AO
Relief Damper | Building static pressure | DP transducer between representative space and outdoors | AI
Relief Fan | Relief-fan start/stop | Connect to VFD Run | DO
Relief Fan | Relief-fan status | Connect to VFD Status | DI
Relief Fan | Relief-fan speed | Connect to VFD Speed | AO
Relief Fan | Relief damper open/close | Two position actuator | DO
Relief Fan | Building static pressure | DP transducer between representative space and outdoors | AI
Retrun Fan | Return fan start/stop | Connect to VFD Run | DO
Retrun Fan | Return-fan status | Connect to VFD Status | DI
Retrun Fan | Return-fan high-static alarm reset | Dry contact to 120V or 24V control circuit | DO
Retrun Fan | Return-fan speed | Connect to VFD Speed | AO
Return Fan Airflow Tracking | Supply airflow (if airflow tracking logic used) | Airflow measurement station at supply fan (or sum of VAV zones) | AI
Return Fan Airflow Tracking | Return airflow (if airflow tracking logic used) | Airflow measurement station at return fan | AI
Return Fan Building Static | Return-fan discharge static pressure | DP transducer at fan | AI
Return Fan Building Static | Exhaust damper | Modulating actuator | AO
Return Fan Building Static | Building static pressure | DP transducer between representative space and outdoors | AI
Split Econ | Minimum outdoor air damper | Modulating actuator | AO
Split Econ | Minimum outdoor airflow | Airflow measurement station | AI
SINGLE ZONE AHU
Required | Description | Device | Type
CO2 DCV | Zone CO2 level | Room CO2 sensor | AI
DX | Cooling signal | Variable-capacity compressor | AO
Final Filter | Filter pressure drop | DP transducer across filter | AI
Hydronic | Cooling signal | Modulating CHW valve | AO
Intermidiate Filter | Filter pressure drop | DP transducer across filter | AI
Occupancy DCV | Occupancy sensor | Occupancy sensor | DI
Outdoor AFM | Outdoor Airflow | Airflow measurement station | AI
Prefilter | Filter pressure drop | DP transducer across filter | AI
Preheat Coil | Heating signal | Modulating HW valve | AO
Preheat Coil Electric | Heating signal | Modulating electric heating coil | AO
R | Supply fan start/stop | Connect to VFD Run | DO
R | Supply fan speed | Connect to VFD Speed | AO
R | Supply fan status | Connect to VFD Status | DI
R | Supply air temperature | Duct temperature sensor (probe or averaging at designer’s discretion) | AI
R | Outdoor/return air damper | Modulating actuators | AO
R | Outdoor air temperature | Temperature sensor at outdoor air intake | AI
R | Mixed air temperature | Averaging temperature sensor | AI
R | Return air temperature | Duct temperature sensor | AI
R | Zone temperature | Room temperature sensor | AI
Reheat Coil | Heating signal | Modulating HW valve | AO
Reheat Coil Electric | Heating signal | Modulating electric heating coil | AO
Relief Damper | Relief damper | Modulating actuator | AO
Relief Fan | Relief-fan start/stop | Connect to VFD Run | DO
Relief Fan | Relief-fan status | Connect to VFD Status | DI
Relief Fan | Relief-fan speed | Connect to VFD Speed | AO
Relief Fan | Relief-damper open/close | Two position actuator | DO
Return Fan | Return fan start/stop | Connect to VFD Run | DO
Return Fan | Return-fan status | Current VFD Status | DI
Return Fan | Return-fan speed | Connect to VFD Speed | AO
Return Fan Airflow Tracking | Exhaust air damper | Two position actuator | DO
Return Fan Building Static | Return Fan Discharge Static Pressure | Differential pressure transducer at fan | AI
Return Fan Building Static | Exhaust Air Damper | Modulating actuator | AO
Return Fan Building Static | Building Static Pressure | Differential pressure transducer between representative space and outdoors | AI
Window DCV | Window switch | Window switch | DI
Zone Tstat | Local override | Zone thermostat override switch | DI
Zone Tstat | Zone temperature setpoint adjustment | Zone thermostat adjustment | AI
CONSTANT SPEED EXHAUST FAN
Required | Description | Device | Type
R | Exhaust Fan Start/Stop | Connect to motor starter | DO
R | Exhaust Fan Status | Current switch | DI
BY TEMP | Zone Temperature | Room temperature sensor | AI

## Sequences
MULTIZONE AHU
Required | Description | Sequence
R | Supply Fan Control
R | Supply Air Temperature Control
OA Damper | Minimum Outdoor Airflow Setpoints
OA Damper | Minimum OA Saperate Damper and airflow tracking
OA Damper | Minimum OA common Damper and airflow tracking
Relief Damper | Control of Actuated Relief Dampers without Fans
Relief fan | Relief fan control
Return Fan | Building pressure Control
Return Fan | Airflow tracking Control
Freeze Protection |  | If the supply air temperature drops below 4.4°C (40°F) for 5 minutes, send two (or more, as required to ensure that heating plant is active) heating hot-water plant requests, override the outdoor air damper to the minimum position, and modulate the heating coil to maintain a supply air temperature of at least 6°C (42°F). Disable this function when supply air temperature rises above 7°C (45°F) for 5 minutes. If the supply air temperature drops below 3.3°C (38°F) for 5 minutes, fully close both the economizer damper and the minimum outdoor air damper for 1 hour and set a Level 3 alarm noting that minimum ventilation was interrupted. After 1 hour, the unit shall resume minimum outdoor air ventilation and enter the previous stage of freeze protection. If it is warm enough that the SAT rises above 7°C (45°F) with minimum ventilation, the unit will remain in Stage 1 freeze protection for 5 minutes then resume normal operation. Upon signal from the freeze-stat (if installed), or if supply air temperature drops below 3.3°C (38°F) for 15 minutes or below 1°C (34°F) for 5 minutes, shut down supply and return/relief fan(s), close outdoor air damper, open the cooling-coil valve to 100%, and energize the CHW pump system. Also send two (or more, as required to ensure that heating plant is active) heating hot-water plant requests, modulate the heating coil to maintain the higher of the supply air temperature or the mixed air temperature at 27°C (80°F), and set a Level 2 alarm indicating the unit is shut down by freeze protection. If a freeze-protection shutdown is triggered by a low air temperature sensor reading, it shall remain in effect until it is reset by a software switch from the operator’s workstation. (If a freeze-stat with a physical reset switch is used instead, there shall be no software reset switch.)
Alarms
R | Automatic Fault Detection and Diagnostics
R | Testing or Commissioning Overrides
R | Plant Requests